## MakeReadyData
Connection ID | Operation Number | Attachment Action | Pole Owner | Pole # | SCID | Pole Structure | Proposed Riser | Proposed Guy | PLA (%) with proposed attachment | Construction Grade of Analysis | Height Lowest Com | Height Lowest CPS Electrical | Data Category | Bearing | Attacher Description | Attachment Height - Existing | Attachment Height - Proposed | Mid-Span (same span as existing) | One Touch Transfer | Remedy Description | Responsible Party | Existing CPSE Red Tag on Pole | Pole Data Missing in GIS | CPSE Application Comments | Movement Summary | From Pole | To Pole
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | CPS ENERGY Neutral | 29'-6" |  |  | Make Ready Simple | Raise CPS ENERGY Neutral 21" from 27'-1" to 29'-4" Raise CPS ENERGY Supply Fiber 36" from 24'-12" to 27'-12" Raise CPS ENERGY Neutral 21" from 27'-1" to 29'-4" Raise CPS ENERGY Supply Fiber 36" from 24'-12" to 27'-12" | New Attacher | NO |  |  | Install proposed Charter Fiber Optic Com at 24'-7" Raise CPS ENERGY Neutral 21" from 27'-1" to 29'-4" Raise CPS ENERGY Supply Fiber 36" from 24'-12" to 27'-12" Raise AT&T Fiber Optic Com 5" from 21'-2" to 22'-9" Raise AT&T Telco Com 29" from 19'-9" to 21'-4" Raise AT&T Com Drop 18" from 14'-5" to 16'-11" Raise CPS ENERGY Neutral 21" from 27'-1" to 29'-4" Raise CPS ENERGY Supply Fiber 36" from 24'-12" to 27'-12" Raise AT&T Fiber Optic Com 5" from 21'-2" to 22'-9" Raise AT&T Telco Com 29" from 19'-9" to 21'-4" Raise AT&T Com Drop 18" from 14'-5" to 16'-11" | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | CPS ENERGY Supply Fiber | 28'-0" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | Charter Fiber Optic Com | 24'-7" |  | 21'-1" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | AT&T Fiber Optic Com | 23'-7" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | AT&T Telco Com | 22'-4" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | AT&T Com Drop | 21'-5" |  | 17'-2" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Main_Attacher |  | AT&T Com Drop | 21'-5" |  | 17'-2" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Header |  | REF () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Attacher |  | CPS ENERGY Neutral | 27'-1" | 29'-4" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Attacher |  | CPS ENERGY Supply Fiber | 24'-12" | 27'-12" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Attacher |  | Charter Fiber Optic Com | 22'-11" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Attacher |  | AT&T Fiber Optic Com | 21'-2" | 22'-9" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Attacher |  | AT&T Telco Com | 19'-9" | 21'-4" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Ref_Span_Attacher |  | AT&T Com Drop | 14'-5" | 16'-11" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Header |  | Backspan () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Attacher |  | CPS ENERGY Neutral | 27'-1" | 29'-4" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Attacher |  | CPS ENERGY Supply Fiber | 24'-12" | 27'-12" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Attacher |  | Charter Fiber Optic Com | 22'-11" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Attacher |  | AT&T Fiber Optic Com | 21'-2" | 22'-9" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Attacher |  | AT&T Telco Com | 19'-9" | 21'-4" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OJ_QO10emfZauaNUM4I | 1 | I | CPS | PL410620 | 001 | 40-4 | No | No | 82.20 | C | 14'-10" | 25'-8" | Backspan_Attacher |  | AT&T Com Drop | 14'-5" | 16'-11" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL410620 | PL398491
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | CPS ENERGY Neutral | 27'-3" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  | Install proposed Charter Fiber Optic Com at 23'-0" Raise AT&T Fiber Optic Com 8" from 22'-8" to 22'-0" Install proposed Charter riser at 22'-0" Raise AT&T Telco Com 8" from 21'-8" to 21'-0" Lower AT&T Fiber Optic Com 16" from 20'-6" to 19'-10" Lower AT&T Telco Com 12" from 18'-5" to 17'-5" | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | CPS ENERGY Neutral | 27'-3" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | CPS ENERGY Supply Fiber | 25'-9" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | Charter Fiber Optic Com | 23'-0" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | AT&T Fiber Optic Com | 22'-8" | 22'-0" |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | Charter riser | 22'-0" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Main_Attacher |  | AT&T Telco Com | 21'-8" | 21'-0" |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Ref_Span_Header |  | REF () |  |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Neutral | 25'-6" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Supply Fiber | 22'-8" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Ref_Span_Attacher |  | AT&T Fiber Optic Com | 20'-6" | 19'-10" |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OP2M3Yf2DfJczUNfA6w | 2 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | NA | NA | Ref_Span_Attacher |  | AT&T Telco Com | 18'-5" | 17'-5" |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | UG
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | CPS ENERGY Neutral | 27'-3" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  | Install proposed Charter Fiber Optic Com at 23'-0" Raise AT&T Fiber Optic Com 8" from 22'-8" to 22'-0" Install proposed Charter riser at 22'-0" Raise AT&T Telco Com 8" from 21'-8" to 21'-0" Lower AT&T Fiber Optic Com 16" from 20'-6" to 19'-10" Lower AT&T Telco Com 12" from 18'-5" to 17'-5" | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | CPS ENERGY Neutral | 27'-3" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | CPS ENERGY Supply Fiber | 25'-9" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | Charter Fiber Optic Com | 23'-0" |  | 18'-8" | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | AT&T Fiber Optic Com | 22'-8" | 22'-0" | 15'-9" | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | Charter riser | 22'-0" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Main_Attacher |  | AT&T Telco Com | 21'-8" | 21'-0" | 14'-8" | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Ref_Span_Header |  | REF () |  |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Ref_Span_Attacher |  | CPS ENERGY Neutral | 25'-6" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Ref_Span_Attacher |  | CPS ENERGY Supply Fiber | 22'-8" |  |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Ref_Span_Attacher |  | AT&T Fiber Optic Com | 20'-6" | 19'-10" |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJxyAJpFgj-CaetpYWz | 3 | I | CPS | PL389359 | 003 | 45-4 | YES (1) | No | 92.00 | C | 17'-8" | 22'-8" | Ref_Span_Attacher |  | AT&T Telco Com | 18'-5" | 17'-5" |  | Upgrade Simple |  | CPS Energy | NO |  |  |  | PL389359 | PL404474
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | CPS ENERGY Neutral | 26'-0" |  |  | Make Ready Simple |  | New Attacher | NO |  |  | Lower AT&T Fiber Optic Com 22" from 22'-9" to 20'-7" Install proposed Charter Fiber Optic Com at 21'-7" Lower AT&T Telco Com 24" from 21'-7" to 19'-7" Lower AT&T Fiber Optic Com 38" from 18'-7" to 15'-9" Lower AT&T Telco Com 36" from 17'-8" to 14'-8" | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | CPS ENERGY Street Light Feed | 26'-0" |  | 24'-6" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | CPS ENERGY Supply Fiber | 24'-6" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | CPS ENERGY street_light | 23'-6" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | CPS ENERGY drip_loop | 23'-0" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | AT&T Fiber Optic Com | 22'-9" | 20'-7" | 17'-6" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | Charter Fiber Optic Com | 21'-7" |  | 20'-7" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Main_Attacher |  | AT&T Telco Com | 21'-7" | 19'-7" | 16'-6" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Backspan_Header |  | Backspan () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Backspan_Attacher |  | CPS ENERGY Neutral | 22'-8" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Backspan_Attacher |  | CPS ENERGY Supply Fiber | 20'-8" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Backspan_Attacher |  | Charter Fiber Optic Com | 18'-8" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Backspan_Attacher |  | AT&T Fiber Optic Com | 18'-7" | 15'-9" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OJ_QKap8_9w_POuOX7d | 4 | I | CPS | PL404474 | 004 | 40-3 | No | No | 62.45 | C | 19'-6" | 25'-6" | Backspan_Attacher |  | AT&T Telco Com | 17'-8" | 14'-8" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL404474 | PL900997
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | CPS ENERGY Neutral | 27'-1" |  |  | Make Ready Complex | Raise CPS ENERGY Street Light Feed 17" from 24'-10" to 25'-5" Raise CPS ENERGY Service 72" from 12'-0" to 18'-0" | CPS Energy | NO |  |  | Lower AT&T Fiber Optic Com 12" from 21'-6" to 20'-6" Install proposed Charter Fiber Optic Com at 21'-6" Install proposed Charter riser at 20'-6" Lower AT&T Telco Com 12" from 20'-6" to 19'-6" Raise CPS ENERGY Street Light Feed 17" from 24'-10" to 25'-5" Lower AT&T Fiber Optic Com 12" from 22'-1" to 21'-1" Lower AT&T Telco Com 12" from 20'-12" to 19'-12" Raise CPS ENERGY Service 72" from 12'-0" to 18'-0" | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | CPS ENERGY Supply Fiber | 25'-10" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | CPS ENERGY drip_loop | 25'-8" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | CPS ENERGY street_light | 25'-0" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | CPS ENERGY drip_loop | 23'-11" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | AT&T Fiber Optic Com | 21'-6" | 20'-6" |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | Charter Fiber Optic Com | 21'-6" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | Charter riser | 20'-6" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Main_Attacher |  | AT&T Telco Com | 20'-6" | 19'-6" |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Header |  | REF () |  |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Neutral | 26'-5" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Street Light Feed | 24'-10" | 25'-5" |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Supply Fiber | 24'-7" |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Attacher |  | AT&T Fiber Optic Com | 22'-1" | 21'-1" |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Attacher |  | AT&T Telco Com | 20'-12" | 19'-12" |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Header |  | REF () |  |  |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OOZIxBTFE8ctJ5d0c0I | 5 | I | CPS | PL900997 | 005 | 45-2 | YES (1) | No | 64.17 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Service | 12'-0" | 18'-0" |  | Make Ready Complex |  | CPS Energy | NO |  |  |  | PL900997 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Main_Attacher |  | CPS ENERGY Neutral | 26'-6" |  |  | Make Ready Simple |  | New Attacher | NO |  |  | Lower AT&T Fiber Optic Com 3" from 22'-10" to 21'-1" Install proposed Charter Fiber Optic Com at 22'-1" Lower AT&T Telco Com 3" from 21'-10" to 20'-1" Install proposed Charter riser at 21'-1" Lower AT&T Fiber Optic Com 59" from 19'-9" to 14'-8" Lower AT&T Telco Com 59" from 19'-4" to 14'-3" Lower AT&T Fiber Optic Com 59" from 19'-9" to 14'-8" Lower AT&T Telco Com 59" from 19'-4" to 14'-3" | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Main_Attacher |  | CPS ENERGY Supply Fiber | 25'-5" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Main_Attacher |  | AT&T Fiber Optic Com | 22'-10" | 21'-1" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Main_Attacher |  | Charter Fiber Optic Com | 22'-1" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Main_Attacher |  | AT&T Telco Com | 21'-10" | 20'-1" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Main_Attacher |  | Charter riser | 21'-1" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Ref_Span_Header |  | REF () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Neutral | 24'-9" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Ref_Span_Attacher |  | CPS ENERGY Supply Fiber | 21'-2" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Ref_Span_Attacher |  | AT&T Fiber Optic Com | 19'-9" | 14'-8" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Ref_Span_Attacher |  | AT&T Telco Com | 19'-4" | 14'-3" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Backspan_Header |  | Backspan () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Backspan_Attacher |  | CPS ENERGY Neutral | 24'-7" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Backspan_Attacher |  | CPS ENERGY Supply Fiber | 21'-1" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Backspan_Attacher |  | AT&T Fiber Optic Com | 19'-9" | 14'-8" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-OPCjr3oYEEY70EImQWq | 6 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | NA | NA | Backspan_Attacher |  | AT&T Telco Com | 19'-4" | 14'-3" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | UG
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Main_Attacher |  | CPS ENERGY Neutral | 26'-6" |  |  | Make Ready Simple |  | New Attacher | NO |  |  | Lower AT&T Fiber Optic Com 3" from 22'-10" to 21'-1" Install proposed Charter Fiber Optic Com at 22'-1" Lower AT&T Telco Com 3" from 21'-10" to 20'-1" Install proposed Charter riser at 21'-1" Lower AT&T Fiber Optic Com 59" from 19'-9" to 14'-8" Lower AT&T Telco Com 59" from 19'-4" to 14'-3" Lower AT&T Fiber Optic Com 59" from 19'-9" to 14'-8" Lower AT&T Telco Com 59" from 19'-4" to 14'-3" | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Main_Attacher |  | CPS ENERGY Supply Fiber | 25'-5" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Main_Attacher |  | AT&T Fiber Optic Com | 22'-10" | 21'-1" | 19'-10" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Main_Attacher |  | Charter Fiber Optic Com | 22'-1" |  | 22'-1" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Main_Attacher |  | AT&T Telco Com | 21'-10" | 20'-1" | 18'-7" | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Main_Attacher |  | Charter riser | 21'-1" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Ref_Span_Header |  | REF () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Ref_Span_Attacher |  | CPS ENERGY Neutral | 24'-9" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Ref_Span_Attacher |  | CPS ENERGY Supply Fiber | 21'-2" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Ref_Span_Attacher |  | AT&T Fiber Optic Com | 19'-9" | 14'-8" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Ref_Span_Attacher |  | AT&T Telco Com | 19'-4" | 14'-3" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Backspan_Header |  | Backspan () |  |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Backspan_Attacher |  | CPS ENERGY Neutral | 24'-7" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Backspan_Attacher |  | CPS ENERGY Supply Fiber | 21'-1" |  |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Backspan_Attacher |  | AT&T Fiber Optic Com | 19'-9" | 14'-8" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012
-ONthXX-ClOLypfLM3eG | 7 | I | CPS | PL370858 | 011 | 45-2 | YES (1) | No | 41.95 | C | 20'-8" | 26'-5" | Backspan_Attacher |  | AT&T Telco Com | 19'-4" | 14'-3" |  | Make Ready Simple |  | New Attacher | NO |  |  |  | PL370858 | PL012